## Page 1
AIR CONDITIONER / HEAT PUMP MODE: COOLING HEATING | [5 empty] | DATE:
Fill in all blanks with the measured data relative to the Mode of operation. Mark position of sov slide in schematic.
REASON FOR SERVICE:
CUSTOMER: |  |  |  | Customer concern:
ADDRESS |  |  |  | DEALER:
CITY |  | ZIP CODE |  | PH: |  | FAX:
EQUIPMENT: | INSTALL DATE: |  |  | SERVICE TECH:
MODEL #O/D |  | SN
|  |  |  | Refrigerant: |  | EQUIP. LOCATION:
MODEL # I/D |  | SN |  | Line Size: Suct: | in. | OD above-below ID
ft
FURNACE COIL# |  | SN |  | Number of elbows | Liq. In. | Vertical Separation
or HEATER M/S |  |  |  | Length | ft. |  | ft
Condenser
|  |  | ` |  | Discharge Air
LOW
HI
INDOOR SECTION
Compressor
Field Installed inter- connecting tubing………..
SUPPLY
AIR
RETURN
AIR
DRIER
MUFFLER
TXV
DRIER
__________F
__________F
__________F
__________F
__________F
__________F
HI
LOW
_________F
__________F
__________F
__________F
___________PSI
________PSI
__________PSI
___________F
__________PSI
___________F
__________F
__________F
________F
___________F
TXV
SERVICE VALVE
SERVICE VALVE
__________F
______Db
______Wb
______Db
______Wb
________F
________F
_________F
OUTDOOR AIR DB
__________F
__________Saturated temp
__________ Saturated temp

## Page2
AIR CONDITIONER / HEAT PUMP MODE: COOLING HEATING
Air Flow: | Required |  | From Service Facts | ELECTRICAL: VOLTAGE MEASUREMENTS:
|  |  | find CFM vs ESP | WHIP WIRE SIZE
| Actual |  | to arrive at actual cfm | VOLTAGE MEASUREMENTS: | NO LOAD |  | OPERATING
LINE VOLTS
supply static
CONTROL VOLTS
return static |  | Total static
|  |  |  | AMPS: | Starting |  | OPERATING
Measure return static upsteam and down stream of Perfect Fit |  |  |  | COMPRESSOR:
ID DIP SWITCHES: (X out if on) 1 2 3 4 5 6 7 8 |  |  |  | COMMON
Filter Condition: | CLEAN | DIRTY | CLOGGED | COMMON TO START
Filter Size: |  | Type:
List all sizes in the system |  |  |  | COMMON TO RUN
CIRCLE APPLICABLE ITEMS:
|  |  |  | START ASSIST EAC | HUMIDIFIER | ZONING | DUAL FUEL
RETURN TEMP |  | INSIDE HOME WET BULB |  | THERMOSTAT #: |  | Mfg.
DRY BULB |  |  |  | Type: | ELECTROMECHANICAL ELECTRONIC
|  |  |  | REFRIGERANT: | Liquid | Suction | Discharge
SUPPLY TEMP |  | INSIDE HOME DRY BULB |  | CIRCLE ONE BELOW: | PSIG | PSIG | PSIG
DRY BULB |  |  |  | R-22 R410A
RETURN TEMP |  | Enthalpy figure from chart on page 3 or 4 |  | Convert saturation temps | 1 | 3
WET BULB |  |  |  | from T/P chart or gauges | °F | °F
From Service Facts find
SUPPLY TEMP |  | Enthalpy figure from chart on page 3 or 4 |  | required gauge pressures
WET BULB |  |  |  | Measure the Line Temp | 2 | 4
[5 empty] | °F | °F | °F
Subtract Enthalpy 2 from 1 |  |  |  | ACT. SUBCOOLING then is |  | SUBCOOLING
Delta H Plugs into Total cooling formula |  |  | Delta H = | 1 MINUS 2
CFM x 4.5 x Delta H = Total BTU |  |  |  | ACT. SUPERHEAT then is | SUPERHEAT |  | °F
4 MINUS 3
|  |  |  | REQUIRED SUBCOOLING | °F | REQ S.H. | °F
Indoor
|  |  |  | OD TEMP | °F Db |  | °F Wb
SERVICE HISTORY:
If you measure superheat at the outdoor unit you will need to keep in mind you are including the suction line. If the suction
superheat seems high for the load on the machine, take suction line temperature reading at the evaporator.
Evaporators with FCCVs will need to be charged using the superheat method. Evaporators with expansion valves will need
to be charged using the subcooling method. |  |  |  | Measure superheat and subcooling when troubleshooting.
OBSERVATION/DIAGNOSIS:

## Page3
Formula Sheet
CFM = Volts X Amps X 3.414/ 1.08 X TD
Example 208V X 24.5 Amps = 5096 / 1000 = 5.096 KW
Notes
| AIR FLOW |  | CFM = | V X A X 3.414 |  | 3.413 BTU Per Watt
| HEAT RISE METHOD |  |  | 1.08 X Delta T |  | 1.08 Specific heat constant
| This works only for the blower tap you currently have powered. |  |  |  |  | Compressor off
| Example | 10KW X 3413 | 34130 |  | 1580 CFM | ALLOW TEMPERATURES TO
|  | 20TD X 1.08 | 21.6 |  |  | STABILIZE
If you are running on the heating tap the heat rise method is telling you heating CFM
If you are running on the cooling tap the heat rise method is telling you cooling CFM
Dip Switch 7 and 8 on a V/S motor are used to set the heating CFM
| TOTAL COOLING CAPACITY: |  |  | 4.5 X CFM X DELTA H = BTUH
DELTA H in BTU/LB
| Example |  |  |  | 74 | RETURN Wb = |  | 37.66
| 4.5 X 1580 X 6.83 =48,561.3 BTUH |  |  |  | 66 | SUPPLY Wb = |  | -30.83
[6 empty] | DELTA H | is = | 6.83
| SENSIBLE CAPACITY |  | TEMP | R-22 | R-410 | TEMP | R-22 | R-410
|  |  | 31 | 56 | 99 | 80 | 143 | 235
1.08 X DELTA T DB X CFM = BTUH |  |  | 32 | 57 | 101 | 85 | 155 | 254
|  |  | 33 | 58 | 103 | 90 | 168 | 274
|  |  | 34 | 60 | 104 | 95 | 181 | 295
Example |  |  | 35 | 61 | 107 | 100 | 195 | 317
1.08x17x1580 = 27686.88 BTUH |  |  | 36 | 62 | 109 | 105 | 210 | 340
|  |  | 37 | 64 | 111 | 110 | 226 | 365
|  |  | 38 | 65 | 113 | 115 | 242 | 390
| 77 | Return Db | 39 | 67 | 115 | 120 | 259 | 417
| 60 | Supply Db | 40 | 68 | 118 | 125 | 277 | 445
| 17 | Delta T Db | 41 | 69 | 120 | 130 | 296 | 475
|  |  | 42 | 71 | 122 | 135 | 316 | 506
|  |  | 43 | 72 | 125
|  |  | 44 | 74 | 127
|  |  | 45 | 76 | 129
|  |  | 46 | 77 | 132
|  |  | 47 | 79 | 134
|  |  | 48 | 80 | 137
|  |  | 49 | 82 | 139
|  |  | 50 | 84 | 142
|  |  | 55 | 92 | 155
|  |  | 60 | 101 | 169
|  |  | 65 | 111 | 184
|  |  | 70 | 121 | 200
|  |  | 75 | 132 | 217
Field Service March2.xls

## Page4
Wet Bulb |  |  |  | BTU PER POUND OF DRY AIR (Enthalpy)
| 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
51 | 20.86 | 20.92 | 20.98 | 21.04 | 21.09 | 21.15 | 21.21 | 21.26 | 21.32 | 21.38
52 | 21.44 | 21.49 | 21.55 | 21.6 | 21.66 | 21.72 | 21.78 | 21.83 | 21.89 | 21.95
53 | 22.02 | 22.06 | 22.12 | 22.19 | 22.24 | 22.3 | 22.36 | 22.43 | 22.49 | 22.55
54 | 22.62 | 22.68 | 22.74 | 22.8 | 22.86 | 22.92 | 22.98 | 23.04 | 23.11 | 23.16
55 | 23.22 | 23.28 | 23.34 | 23.4 | 23.46 | 23.52 | 23.58 | 23.64 | 23.71 | 23.77
56 | 23.84 | 23.9 | 23.96 | 24.03 | 24.09 | 24.15 | 24.21 | 24.28 | 24.34 | 24.4
57 | 24.48 | 24.53 | 24.59 | 24.66 | 24.72 | 24.79 | 24.85 | 24.92 | 24.99 | 25.05
58 | 25.12 | 25.18 | 25.25 | 25.32 | 25.38 | 25.45 | 25.51 | 25.58 | 25.65 | 25.71
59 | 25.78 | 25.85 | 25.91 | 25.99 | 26.06 | 26.12 | 26.19 | 26.26 | 26.33 | 26.39
60 | 26.46 | 26.53 | 26.6 | 26.67 | 26.74 | 26.81 | 26.88 | 26.94 | 27.01 | 27.08
61 | 27.15 | 27.21 | 27.28 | 27.35 | 27.42 | 27.48 | 27.55 | 27.62 | 27.69 | 27.76
62 | 27.85 | 27.92 | 28 | 28.07 | 28.14 | 28.21 | 28.29 | 28.36 | 28.43 | 28.5
63 | 28.57 | 28.65 | 28.72 | 28.79 | 28.86 | 28.94 | 29.01 | 29.08 | 29.16 | 29.23
64 | 29.31 | 29.38 | 29.45 | 29.53 | 29.6 | 29.68 | 29.76 | 29.83 | 29.91 | 29.98
65 | 30.06 | 30.13 | 30.21 | 30.29 | 30.37 | 30.45 | 30.52 | 30.6 | 30.68 | 30.76
66 | 30.83 | 30.92 | 31 | 31.07 | 31.15 | 31.23 | 31.31 | 31.39 | 31.47 | 31.54
67 | 31.62 | 31.7 | 31.77 | 31.85 | 31.93 | 32.01 | 32.09 | 32.17 | 32.25 | 32.33
68 | 32.42 | 32.51 | 32.59 | 32.67 | 32.76 | 32.84 | 32.92 | 33.01 | 33.09 | 33.17
69 | 33.25 | 33.34 | 33.42 | 33.5 | 33.59 | 33.67 | 33.75 | 33.84 | 33.92 | 34.01
70 | 34.09 | 34.17 | 34.26 | 34.34 | 34.43 | 34.51 | 34.6 | 34.69 | 34.77 | 34.86
71 | 34.95 | 35.04 | 35.13 | 35.22 | 35.31 | 35.4 | 35.48 | 35.57 | 35.66 | 35.74
72 | 35.83 | 35.92 | 36.01 | 36.1 | 36.19 | 36.27 | 36.37 | 36.46 | 36.55 | 36.65
73 | 36.74 | 36.83 | 36.92 | 37.02 | 37.11 | 37.21 | 37.3 | 37.39 | 37.48 | 37.57
74 | 37.66 | 37.76 | 37.85 | 37.94 | 38.04 | 38.14 | 38.23 | 38.33 | 38.43 | 38.52
75 | 38.61 | 38.71 | 38.8 | 38.9 | 38.99 | 39.09 | 39.18 | 39.28 | 39.37 | 39.47
76 | 39.57 | 39.67 | 39.77 | 38.87 | 39.97 | 40.07 | 40.17 | 40.27 | 40.38 | 40.48
77 | 40.57 | 40.68 | 40.78 | 40.88 | 40.98 | 41.08 | 41.18 | 41.28 | 41.38 | 41.48
78 | 41.58 | 41.69 | 41.79 | 41.89 | 42 | 42.1 | 42.2 | 42.31 | 42.41 | 42.52
79 | 42.62 | 42.73 | 42.83 | 42.94 | 43.05 | 43.15 | 43.26 | 43.37 | 43.48 | 43.59
80 | 43.69 | 43.81 | 43.91 | 44.02 | 44.13 | 44.24 | 44.36 | 44.46 | 44.57 | 44.68
81 | 44.78 | 44.89 | 45 | 45.11 | 45.23 | 45.34 | 45.45 | 45.57 | 45.68 | 45.8
82 | 45.9 | 46.02 | 46.13 | 46.24 | 46.35 | 46.47 | 46.58 | 46.69 | 46.71 | 46.82
83 | 47.04 | 47.16 | 47.28 | 47.4 | 47.52 | 47.63 | 47.75 | 47.87 | 47.99 | 48.1
84 | 48.22 | 48.34 | 48.46 | 48.58 | 47.7 | 48.82 | 48.94 | 49.06 | 49.19 | 49.31
85 | 49.43 | 49.56 | 49.68 | 49.7 | 49.92 | 50.05 | 50.17 | 50.29 | 50.41 | 50.54
To find total capacity of an air conditioning unit during cooling operation
| Measure air entering the coil in Wet Bulb. |  |  |  | Consult this chart and find the equivalent Enthalpy figure
| Measure air leaving the coil in Wet Bulb. |  |  |  | Consult this chart and find the equivalent Enthalpy figure
Measure the cfm passing through the coil
| Plug these figures into the following formula |  |  |  | CFM x 4.5 x change in Enthalpy = Total Heat
| Example: |  |  |  | CFM measured air flow is 1200
| Entering WB temp is 67 degrees |  |  |  | This is an enthalpy of 31.62 btu per pound of dry air
| Leaving WB temp is 57 degrees |  |  |  | This is an enthalpy of 24.48 btu per pound of dry air
Enthalpy change is 7.14 btu per pound of dry air
1200 x 4.5 x 7.14 equals 38556 Btu total heat content